## damages
Building ID | NISTIR Classification | Component Name | Damage State | Nate
A3 | B2011.021a | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | 0
A3 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0 | I might call this a storefront based on the ppt picture
B3 | Hazus | Stucco over masonry | 0
B3 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1 | I might call this a storefront based on the ppt picture
C1 | Hazus | Masonry Cladding | 0 | I feel like this building is probably wood and not URM, but I can't say for certain, so makes sense to go with the description from ATC. It might be masonry veneer rather than actual masonry, but would leave as is.
C1 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1
C3 | Hazus | URM walls | 0
C3 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0
C4 | B2011.201a | Precast Concrete Panels 4.5 inches thick - in plane deformation | 0
C4 | Hazus | Windows | 0
C4 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0
E1 | Hazus | URM | 2
E1 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0
F2 | B2011.011b | Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 0 | likely stucco over metal studs? Or wood studs? Probably metal I think?
F2 | Hazus | Windows | 0
F2 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0 | storefront? Windows?
I4 | Hazus | Masonry | 0
I4 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0
J1 | Hazus | Stucco over masonry | 1
J1 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1
J2 | Hazus | Ceramic Tile | 0
J2 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 2
J3 | Hazus | URM walls | 0
J3 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 2
J5 | Hazus | Stucco over brick | 0
J5 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1 | I don't see a curtain wall here. I would have storefront and windows
J6 | Hazus | Stucco over masonry | 0
J6 | Hazus | Windows | 3
K1 | B2011.201a | Precast Concrete Panels 4.5 inches thick - in plane deformation | 0 | I would consider both in-plane and out-of-plane, thought out of plane damage is acceleration based rather than drift based
K1 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0
L5 | Hazus | Concrete Walls | 0 | Seems odd that this would be precast concrete. I wonder if it's actually masonry rather than concrete, but could be concrete. Regardless, should probably use hazus concrete wall instead.
L5 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0
L7 | B2011.111 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | 0
L7 | Hazus | Windows | 0
M10 | B2011.111 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | 0 | no hold-downs seems reasonable for 1960s construction
M10 | Hazus | Windows | 0
M10 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0 | I'd call this a storefront
M2 | B2011.111 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | 0 | no hold-downs seems reasonable for 1960s construction
M2 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 0 | I might call this a storefront based on the ppt picture
L1 | B2011.011b | Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 1 | why b and not a?
L1 | Hazus | Normal windows | 0
Z1 | B2011.011a | Exterior Wall - Cold formed steel walls with flat strap X-bracing, interior - gypsum board | 1
Z1 | Hazus | Stone Veneer | 2
Z1 | Hazus | Normal windows | 0
I1 | Hazus | URM walls | 2 | Should account for the steel frame underneath somehow? This will affect overall building susceptibility
I1 | Hazus | Windows | 0
I1 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1 | also include windows as a separate item?
Z3 | Hazus | Brick veneer | 4
Z3 | Hazus | Windows | 4
Z6 | B2011.201a | Precast Concrete Panels 4.5 inches thick - in plane deformation | 0

## buildings
Building ID | Building Type | Construction Year | Inspection Type | Existing Tag | Building Name / Alt Names | General Damage Classification (Structural) | General Damage Classification (Nonstructural) | Comments about General Damage | Cladding Separation or Damage | Windows Damage | Comments about Nonstructural Damage | Notes from Casey
A3 | S3 | 2014 | Ext. & Int. | None | Burgerfi | None(N) | Insignificant (I) | Exterior Non-building Damage: Retaining wall displacement Broken water line at shifted soda fountains, cracked slab-on-grade. Retaining wall outside building shifted away from building. | 0- | 0- | Broken water pipe at shifted soda machine. Water flowed downstairs. Turned off at 4am. Minimal damage. | None
B3 | RM1L | 1960 | Ext. Only | None |  | Insignificant (I) | None(N) | No access to roof/interior so hard to tell | 0- | 20- | Cladding Separation or Damage: Some cracks in stucco No contents in bldg | Some of the windows in the google maps photo already look broken, so it might not be from the earthquake. Also, the inspector listed the nonstructural damage as “None”, so the 20% of windows damaged could have already been damaged prior.
C1 | URML | 1900 | Ext. & Int. | Red -> Green | Small World Café, Lothe's Salad, Nomad's | Insignificant (I) | Insignificant (I) |  | 0- | 30- | glazing at corner/front (Nomadic Beads) significant (3 out of 4 large panes) local plaster spalled on rear back wall (masonry appears intact in limited observation) | None
C3 | URML | 1900 | Ext. Only | Yellow -> Green | Inti | Insignificant (I) | Unknown (UNK) | ATC-13 Damage State, Nonstructural: 2 (Glazing) Balance not known | 0- | 80- | Windows Damage: Glass storefront | None
C4 | PC1 | 1965 | Ext. & Int. | Yellow | Carithers Building | None (N) | Moderate (M) | [Blank] | 0 | 0 | "some asbestos exposedPartitions Damage: Moderate- Water damage and modular furniture" | Could be a yellow tag due to exposed asbestos and water damage
E1 | URML | 1904 | Ext. & Int. | Red | Center Bldg. | Heavy (H) | Moderate (M) | "Pounding w/ E2, rocks fell outSouth URM wall fell into parking lotNorth URM wall (seen from E2) has X-crack" | 5 | 0 | plaster ceilings are caving in | None
F2 | S2L | 1970 | Ext. & Int. | Green | County Offices | Minor (m) | Minor (m) | [Blank] | 0 | 0 | "Extensive piping damage @ penthouseExtensive clg damage, 3rd Floor. Heavy clg damage 3rd FloorHeavy contents damage 3rd FloorDamage to floor to clg mod. partitions 3rd Floor" | Cladding Damage % and Comment contradict each other. Use number and general damage classification
I4 | RM1L | 1962 | Ext. & Int. | Green | Darin's Gun Exchange | None(N) | None(N) | [Blank] | 0 | 0 | [Blank] | None
J1 | RM2L | 1963 | Ext. & Int. | Green | Ceja Vineyards | Insignificant (I) | Insignificant (I) | [Blank] | 0 | 15 | Cracks in stucco on exterior, cracks in ceilings & partitions + broken windows | None
J2 | URML | 1920 | Ext. Only | Red |  | Unknown (UNK) | Unknown (UNK) | "No damage observed in limited exterior survey. South side of blds & portion of North side visible. " | 0 | 45 | "Limited review of nonstructural through window. Mostly empty bldg. unclear if damage to ceiling is from eq or bldg being abandoned. " | None
J3 | URML | 1910 | Ext. Only | Red | Wildcat | Unknown (UNK) | Unknown (UNK) | No damage observed in limited exterior survey. Damage may be moderate to heavy. Further inspection would be required south side of bldg only side visible. | 0 | 33 | No review of nonstructural as interior was not visible and roof not accessible. | None
J5 | RM1L | 1960 | Ext. Only | Red |  | Unknown (UNK) | Unknown (UNK) | "No damage observed in limited exterior survey. East side of bldg only side visible. " | 0 | 20 | Limited review of nonstructural through south side windows. | None
J6 | URML | 1920 | Ext. & Int. | None | Merrill's Rx | Insignificant (I) | Minor (m) | Pounding Damage: minor | 0 | 50 | some lights are damaged and a small portion of the ceiling is damaged but unclear if from EQ. | None
K1 | PC1 | 1960 | Ext. & Int. | Green | Kohls | Insignificant (I) | Minor (m) | Crack in slab on grade around interior perimeter, presumably at interface with strip footing; slab side lower than chunk of concrete fell through ceiling near NE of building. | 0-NA | 0 | "~36 ceiling tiles fell -one automatic sliding glass exit door came off track and was not operable. ~12 floor tiles heavedcandles and glass merchandise fell; ~2 unanchored storage racks fellHanging TV monitors damaged slightly. " | None
L5 | C2L | 1940 | Ext. & Int. | Green |  | None(N) | None(N) | [Blank] | 0-NA | 0 | [Blank] | None
L7 | W1 | 1936 | Ext. & Int. | Green |  | Insignificant (I) | Insignificant (I) | Some reparable cracking in exterior stucco...may not even be repaired | 0 | 8 | minor sheetrock + contents damage. Very little Windows Damage: 1 window @ storefront | None
M10 | W2 | 1960 | Ext. & Int. | None |  | Insignificant (I) | Insignificant (I) | No structural damage observed. Very minor cracking in exterior wall stucco. | 0 | 5 | Some cracks in partitions. Some windows broken. 1 window fell in and damage bike. One air pipe broke in auto repair shop but it was replaced w/ no other damage. | None
M2 | W1 | 1940 | Ext. & Int. | None | Napa Valley Classics, Lloose Caboose Hobbies | None(N) | Insignificant (I) | [Blank] | 1 | 5 | "contents: $5000 @ Hobbies store lost (toy trains) some collectables @ motorcycle store Cladding Separation or Damage: <1%" | None
L1 | S2L | 2002 | Ext. & Int. | Yellow | [6 empty] | “In general, very little nonstructural damage to the building was observed. There was almost no drywall damage observed on the first floor, and no ceiling damage reported. As noted above, there was damage to the light-frame furring at the third floor north wall, in the vicinity of one brace. Along the north wall, damage to the exterior wall occurred when the out-of-plane wall anchors of the adjacent building struck the drywall (Figure 4-5). No damage to equipment or piping, including the fire sprinkler system, was reported. “ | None
Z1 | S1L | 2008 | Ext. & Int. | Red -> Green | [6 empty] | “The south exterior wall of the building, which contains large sections of solid wall, suffered the most significant damage (Figures 4-7 and 4-8). The wall, constructed with metal studs sheathed on the exterior with 5/8 inch gypsum fire-rated wallboard and approximately 1 1/4 inch of cement plaster (Figure 4-9), does not appear to have been detailed to accommodate story drift through a sliding or 4-6 4: Performance of Selected Buildings FEMA P-1024 yielding mechanism. Consequently, the wall suffered several types of damage due to in-plane displacement, including failure of connections at the floors causing separation and bowing of the wall (Figure 4-10 and 4-11), distressed studs, and plaster and gypsum wallboard cracking (Figure 4-12). In addition, the following damage was reported and/or observed: (1) Some adhered cast-stone foam-backed veneer and stone veneer became dislodged (Figure 4-12); (2) a water heater at the second floor, which was reportedly strapped, became dislodged, broke a water pipe and caused water to flow into an electrical room below where metering equipment suffered water damage; and (3) the glass in an interior room partition was broken. “ | None
I1 | S5L | 1914 | Ext. & Int. | Yellow | "playful Digs" | Insignificant (I) | Insignificant (I) | Few bricks fell from façade | 0-NA | 30- | Loss of contents- convection oven leg failure cracking of plaster on walls Windows Damage: first floor only | Yellow tagged due to falling bricks above entrance
Z3 | S5L | 1933 | Ext. & Int. | Red | [6 empty] | “Significant cracking was observed to the exterior brick veneer of the building, which is mostly a true veneer with anchor ties. Interior finish on exterior wall and interior partitions are hollow clay tile with plaster. These were heavily damaged, especially near the front corner piers, with significant fallen clay tile units and debris. Plaster ceilings were damaged, especially in the vicinity of the corner piers. Heavy glazing damage was also observed (Figure 4-26).“ | None
Z6 | PC1 | 1973 | Ext. & Int. | Yellow | [6 empty] | “One unbraced sprinkler line broke (Figure 4-29), and water ran for several hours. The lightly strapped hot water heater overturned breaking a water line but not the gas line, which had a flexible connection. There was damage to refrigeration equipment. The suspended acoustic tile ceiling was severely damaged, including substantial loss of tiles and failures in the grid, requiring replacement of the entire ceiling (Figure 4-30). Some light fixtures were dislodged at their connections to the struts supporting them. Some unanchored store fixtures shifted or overturned. At one aisle, all of the fixtures along one side overturned into the aisle; there was substantial loss of contents from shelves, and virtually all the product was lost (Figure 4-31). “ | None

## buildings summary
Building Type |  | Existing Tag |  | Inspection Type |  | Construction Year
W1 | 2 | Green | 6 | Ext. & Int. | 18 | Pre 1941 | 11
W2 | 1 | Yellow | 4 | Ext. Only | 5 | 1941 - 1975 (inclusive both sides) | 9
S1L | 1 | Red | 5 | Total: | 23 | After 1975 | 3
S1M | 0 | Green -> Yellow | 0 |  |  | Total: | 23
S1H | 0 | Green -> Red | 0
S2L | 2 | Yellow -> Green | 1
S2M | 0 | Yellow -> Red | 0
S2H | 0 | Red -> Green | 2
S3 | 1 | Red -> Yellow | 0
S4L | 0 | None | 5
S4M | 0 | Total: | 23
S4H | 0
S5L | 2
S5M | 0
S5H | 0
C1L | 0
C1M | 0
C1H | 0
C2L | 1
C2M | 0
C2H | 0
C3L | 0
C3M | 0
C3H | 0
PC1 | 3
PC2L | 0
PC2M | 0
PC2H | 0
RM1L | 3
RM1M | 0
RM2L | 1
RM2M | 0
RM2H | 0
URML | 6
URMM | 0
MH | 0
Total = | 23

## Hazus Building Types
# | Building Type | Description | Height
|  |  | Range |  | Typical
|  |  | Name | Stories | Stories | Feet
1 | W1 | Wood, Light Frame (<= 5,000 sq. ft.) |  | 1 - 2 | 1 | 14
2 | W2 | Wood, Commercial & Industrial (> 5,000 sq. ft.) |  | All | 2 | 24
3 | S1L | Steel Moment Frame | Low-Rise | 1 - 3 | 2 | 24
4 | S1M |  | Mid-Rise | 4 - 7 | 5 | 60
5 | S1H |  | High-Rise | 8+ | 13 | 156
6 | S2L | Steel Braced Frame | Low-Rise | 1 - 3 | 2 | 24
7 | S2M |  | Mid-Rise | 4 - 7 | 5 | 60
8 | S2H |  | High-Rise | 8+ | 13 | 156
9 | S3 | Steel Light Frame |  | All | 1 | 15
10 | S4L | Steel Frame with Cast-in-Place Concrete Shear Walls | Low-Rise | 1 - 3 | 2 | 24
11 | S4M |  | Mid-Rise | 4 - 7 | 5 | 60
12 | S4H |  | High-Rise | 8+ | 13 | 156
13 | S5L | Steel Frame with Unreinforced Masonry Infill Walls | Low-Rise | 1 - 3 | 2 | 24
14 | S5M |  | Mid-Rise | 4 - 7 | 5 | 60
15 | S5H |  | High-Rise | 8+ | 13 | 156
16 | C1L | Concrete Moment Frame | Low-Rise | 1 - 3 | 2 | 20
17 | C1M |  | Mid-Rise | 4 - 7 | 5 | 50
18 | C1H |  | High-Rise | 8+ | 12 | 120
19 | C2L | Concrete Shear Walls | Low-Rise | 1 - 3 | 2 | 20
20 | C2M |  | Mid-Rise | 4 - 7 | 5 | 50
21 | C2H |  | High-Rise | 8+ | 12 | 120
22 | C3L | Concrete Frame with Unreinforced Masonry Infill Walls | Low-Rise | 1 - 3 | 2 | 20
23 | C3M |  | Mid-Rise | 4 - 7 | 5 | 50
24 | C3H |  | High-Rise | 8+ | 12 | 120
25 | PC1 | Precast Concrete TiltUp Walls |  | All | 1 | 15
26 | PC2L | Precast Concrete Frames with Concrete Shear Walls | Low-Rise | 1 - 3 | 2 | 20
27 | PC2M |  | Mid-Rise | 4 - 7 | 5 | 50
28 | PC2H |  | High-Rise | 8+ | 12 | 120
29 | RM1L | Reinforced Masonry Bearing Walls with Wood or Metal Deck Diaphragms | Low-Rise | 1 - 3 | 2 | 20
30 | RM1M |  | Mid-Rise | 4+ | 5 | 50
31 | RM2L | Reinforced Masonry Bearing Walls with Precast Concrete Diaphragms | Low-Rise | 1 - 3 | 2 | 20
32 | RM2M |  | Mid-Rise | 4 - 7 | 5 | 50
33 | RM2H |  | High-Rise | 8+ | 12 | 120
34 | URML | Unreinforced Masonry Bearing Walls | Low-Rise | 1 - 2 | 1 | 15
35 | URMM |  | Mid-Rise | 3+ | 3 | 35
36 | MH | Mobile Homes |  | All | 1 | 10